Lead in Drinking Water – Public and Nonpublic Schools

**IMPORTANT NOTICE: ELEVATED WATER SAMPLE RESULT(S)**

**Powhatan Elementary School**

**ELEVATED LEAD WATER SAMPLE RESULT(S)**

All Maryland public and nonpublic schools are required to sample all drinking water sources for the presence of lead pursuant to the Code of Maryland Regulations. On December 14, 2019, 40 water samples were collected from Powhatan Elementary School. Of these water samples, nine (9) had levels of lead exceeding the action level of 20 parts per billion (ppb) for lead in drinking water in school buildings. These were samples from fixtures that were repaired in the past year. The elevated lead results from the sample(s) collected at Powhatan Elementary School were as follows:

31.4 parts per billion (ppb) Bubbler, Room 2

33.9 parts per billion (ppb) Tap, Room 2, Handsink

23.3 parts per billion (ppb) Fountain, Hallway by Room 3

21.9 parts per billion (ppb) Bubbler, Room 5

21.4 parts per billion (ppb) Bubbler, Room 6

24.3 parts per billion (ppb) Bubbler, Room K1, Right side

58.0 parts per billion (ppb) Bubbler, Room 13

31.4 parts per billion (ppb) Bubbler, Room 16

94.4 parts per billion (ppb) Bubbler, Room 18

**IMMEDIATE ACTIONS TAKEN**

Flushed samples were taken from all fixtures with elevated levels, which were then turned off on February 18, 2020. A work order was submitted to have these fixtures remediated. Bottled water will continue to be provided for drinking.

**NEXT STEPS**

The fixture will be remediated. It will not be returned to operation until it has been sampled and found to be below the action level. Upon completion of this action a notification will be sent to the school community. Bottled drinking water will continue to be provided until all drinking water fixtures are sampled and found to be below the action level.

**ACTION LEVEL (AL)**

The AL is 20 ppb for lead in drinking water in school buildings. The AL is the concentration of lead which, if exceeded, triggers required remediation.

**LOCAL AND FEDERAL DRINKING WATER STANDARDS**

Without being required to do so, BCPS has tested school drinking fountains for lead since 2016. There are no federal regulations for schools regarding drinking water. The federal Clean Drinking Water Act requires public water systems to test for lead. Nine of our schools have well systems, and those systems have tested for lead as required.

**HEALTH EFFECTS OF LEAD**

Lead can cause serious health problems if too much enters your body from drinking water or other sources. It can cause damage to the brain and kidneys, and can interfere with the production of red blood cells that carry oxygen to all parts of your body. The greatest risk of lead exposure is to infants, young children, and pregnant women. Lead is stored in the bones and it can be released later in life. During pregnancy, the fetus receives lead from the mother’s bones, which may affect brain development. Scientists have linked the effects of lead on the brain with lowered IQ in children. Adults with kidney problems and high blood pressure can be affected by low levels of lead more than healthy adults.

**SOURCES OF HUMAN EXPOSURE TO LEAD**

There are many different sources of human exposure to lead. These include: lead-based paint,

lead-contaminated dust or soil, some plumbing materials, certain types of pottery, pewter, brass fixtures, food, and cosmetics, exposure in the work place and exposure from certain hobbies, brass faucets, fittings, and valves. According to the Environmental Protection Agency (EPA), 10 to 20 percent of a person’s potential exposure to lead may come from drinking water, while for an infant consuming formula mixed with lead-containing water this may increase to 40 to 60 percent.

**HOW CONSUMERS CAN REDUCE EXPOSURE TO LEAD IN DRINKING WATER**

1. Run your water to flush out lead**:** If water hasn’t been used for several hours, run water for 15 to 30 seconds or until it becomes cold or reaches a steady temperature before using it for drinking or cooking.
2. Use cold water for cooking and preparing baby formula. If lead was present in the plumbing, it would dissolve more easily in hot water.

*Please note that boiling the water will not reduce lead levels.*

**ADDITIONAL INFORMATION**

1. For additional information, please contact David Glassman, Supervisor, Environmental Services at 443.809.6310 or [dglassman2@bcps.org](mailto:dglassman2@bcps.org).
2. For additional information about reducing lead exposure around your home/building and the health effects of lead, visit EPA’s website at [www.epa.gov/lead](http://www.epa.gov/lead).
3. If you are concerned about exposure, contact your healthcare provider. If you do not have a healthcare provider, please contact the Baltimore County Department of Health at 410.887.3725.